Appendix 1 – Particular Conditions and Technical Specifications

Tender for

Supply and Deployment of Automated Power Station

for High Anti-Corruption Court

Section A:	Particular Conditions

Section B:	Technical Specifications

- The Buyer’s Requirements

- The Supplier’s Technical Specifications

All sections which the Tenderer must complete are marked in yellow.

## Section A: Particular Conditions

### General background

The HACC’s premises at 42-A Khreshchatyk Street require the supply and installation of an automated power station (APS) system to ensure stable daily operations. The most optimal technical solution is the placement of the APS on a mobile two-axle trolley with subsequent connection to the building in accordance with international and local standards, as well as all applicable regulations and requirements for such works.

### Recipient

Under this Agreement, the Recipient of the Goods is not the Buyer but:

Name of Recipient: High Anticorruption Court of Ukraine

Name of representative: Oleksandr Hrebennyk

Postal address: Ukraine, Kyiv, 42-A Khreshchatyk street, 01001

Email: o.hrebennyk@vaks.gov.ua

### Place of delivery

The Supplier shall deliver the Goods to:

Name of location: High Anticorruption Court of Ukraine

Name of representative: Oleksandr Hrebennyk

Postal address: Ukraine, Kyiv, 42-A Khreshchatyk street, 01001

Office hours: 9:00-17:00

### Time of delivery

The Supplier shall deliver the equipment and perform the scope of work no later than:

Date: 31 December 2025

Time: 17.00 Kyiv time

Section B – Technical Specifications

The Supplier is obliged to deliver the Goods in accordance with the Buyer’s requirements and the Supplier’s Technical Specifications. In case of conflict between the Buyer’s requirements and the Supplier’s Technical Specifications, the Buyer’s Requirements shall prevail.

### The Buyer’s Requirements

  - Requirements for the Supplier

- The supplier must have successful experience in implementing contracts with international organisations and foundations within the last 5 years.

- The supplier must have at least two specialists with a third-level electrical safety admission (up to 1000 V) (copies of valid certificates must be provided).

- The supplier must have a quality management system certificate compliant with ISO 9001:2015 “Quality Management Systems. Requirements” (a copy of the certificate must be provided).

The quality management system must cover the following areas: design and construction of engineering systems, including engineering infrastructure of data centres and power supply systems.

- The supplier must have an environmental management system certificate compliant with ISO 14001:2015 “Environmental Management Systems. Requirements and guidance for use” (a copy of the certificate must be provided).

The environmental management system must cover the following areas: design and construction of engineering systems, including engineering infrastructure of data centres and power supply systems.

  - Scope of Work

The supply, installation, and commissioning of the Equipment must include the following:

- Delivery of following hardware and components to the HACC:

  - Automated Diesel Power Station (ADPS)

  - Two-axle trolley for housing the proposed ADPS and enabling transportation within a restricted area without registration with the Ministry of Internal Affairs service centres

  - Automatic transfer switch (ATS) panel

  - Power cables, control cables, auxiliary power cables for the ADPS, grounding wires, cable support system components, and grounding system components

Any additional or consumable materials required for the full scope of work shall be provided by the Supplier.

- Installation Works, including the following:

  - Installation of the two-axle trolley intended for housing the proposed ADPS

  - Installation of the ADPS on the trolley

  - Installation of the ATS switchgear in the premises, mounted on the wall near the existing incoming distribution board

  - Installation of a grounding loop at the location of the ADPS on the trolley

  - Installation of the power cable of the required cross-section between the ATS switchgear and the ADPS incoming device. The installation shall be carried out above the suspended ceiling inside the building and along the building façade outside

  - Installation of auxiliary power cables, start control cables, and grounding for the automated diesel power station (ADPS)

  - In the existing incoming distribution board of the facility, reconfiguration of cable jumpers of the power busbars shall be performed, taking into account the integration of ADPS into the facility’s power supply scheme. This must ensure that, in the event of a loss of voltage from the city grid, standby power from the ADPS is supplied to the power busbars feeding the consumers connected to the existing incoming distribution board

All installation works should be performed taking in account the following:

  - Location of the ADPS on the trolley: inner courtyard of the building, asphalted parking area

  - Location of the existing input-distribution switchboard: a room on the first floor of the building

  - Approximate length of the cable route between the ATS switchboard and the ADPS: 80 meters

  - Preliminary location of the grounding loop: at the installation site of the ADPS on the trolley

- Commissioning Works:

  - Commissioning of ADPS

  - Commissioning of the installed ATS switchgear

  - Electrical laboratory testing of the installed cable lines and the grounding loop

  - Conducting basic training for the HACC’s technical personnel and providing guides/instructions for the supplied equipment

All works must be carried out in accordance with the requirements of the current regulatory and legal acts and standards of Ukraine, including: the Electrical Installation Code (PUE), DBN V.2.5-23:2010, DSTU EN 60204, DSTU EN 61439, DSTU IEC 60364, the Rules for the Technical Operation of Electrical Installations of Consumers, and the Rules for the Safe Operation of Electrical Installations of Consumers, as well as other documents regulating the design, installation, and commissioning of electrical installations.

When performing installation and commissioning works and operating equipment, use materials and components that are environmentally friendly, do not harm the environment and do not emit harmful emissions into the environment, and do not require the development of special environmental protection measures. The material waste that occurs during the deployment, such as small pieces of cables and wires of cable ducts of all types, should be disposed by the Supplier of installation works in accordance with the common rules for solid waste disposal.

When performing installation and commissioning works and operating equipment, the Supplier must comply with occupational safety requirements in accordance with DBN A.3.2-2-2009 “Occupational safety standards system. Industrial safety in construction”.

  - Technical Specification of supplies and equipment.

1.3.1 Technical requirements for ADPS:

| Parameter | Characteristics | Requirement |
| --- | --- | --- |
| Design option | Noise-absorbing case | Mandatory |
| ADPS power in standby mode Standby power in accordance with ISO 8528 | 66 kVA/53 kW | Minimum requirement |
| ADPS power in continuous operation mode Prime power in accordance with ISO 8528. | 60 kVA/48 kW | Minimum requirement |
| Output voltage | 400/230V | Required |
| Output frequency | 50 Hz | Required |
| Motor speed | 1500 rpm | Not more |
| Fuel consumption at 100% load in continuous operation mode (Prime) | 14 l/h | Not more |
| Output voltage regulation at constant load with stability maintained within | ± 0.5% | Not more |
| Rotation speed regulation at constant load with output current frequency stability maintained within | ± 0.2% | Not more |
| Sound pressure level at 100% load at a distance of 7 m. | 69 dB (A) | Not more |
| Ability to withstand a load of 100% of maximum power with a decrease in frequency | Yes | Mandatory |
| Output voltage reduction at 100% overload | 0.63 | Not more |
| EMC compatibility of the diesel generator set | BS EN61000-6-4/BS EN61000-6-2 | Mandatory |
| ADPS completeness: |  |  |
| Industrial-grade diesel engine | Yes | Mandatory |
| Number of diesel engine cylinders, placement | 4-cylinder in-line | Mandatory |
| Engine displacement, l | 3.3 | Minimum requirement |
| Synchronous brushless alternator, with self-excitation and automatic voltage regulation | Yes | Mandatory |
| Alternator insulation class | Class H | Not worse |
| Electric starter and charging generator | Yes | Mandatory |
| Standard air, oil, and fuel filters | yes | Mandatory |
| Exhaust noise suppressor | Yes | Mandatory |
| Cooling system radiator mounted on the ADES frame designed for outdoor temperatures | +50°C | Minimum requirement |
| Output protection device | Yes | Mandatory |
| Rechargeable battery with cables and terminals | yes | Mandatory |
| Control panel with LCD monitor | Yes | Mandatory |
| Control panel with fault log; | Yes | Mandatory |
| Control panel must provide: - Monitoring of all critical engine and generator functions - Engine and alternator protection functions - Adjustable delay time for start and stop (cool down) - Remote start capability in automatic mode - Real-time clock for fault and event logging - Data log, including engine operating time and fault history - Recording of recent faults in non-volatile memory - Low fuel warning - Simulator clock for starting/stopping the engine without load - Signal for maintenance based on engine operating time or real-time clock | Yes | Mandatory |
| Electric engine preheating | Yes | Mandatory |
| Automatic battery charger | Yes | Mandatory |
| Steel frame with vibration dampers | Yes | Mandatory |
| Fuel tank built into the ADPS frame | capacity 150 litres | Minimum requirement |
| Requirements for ADPS documentation: |  |  |
| Operating instructions in Ukrainian | Yes | Mandatory |
| Factory test report (provided upon delivery of equipment) | Yes | Mandatory |
| Requirements for ADPS warranty conditions: |  |  |
| ADPS warranty period | 2 years or 400 motor hours (whatever comes first) | Minimum requirement |

1.3.2 Technical requirements for the trolley:

| Parameter | Characteristic | Quantity |
| --- | --- | --- |
| General parameters: |  |  |
| Layout | Two-axle cart, platform between wheels | n/a |
| Suspension | Torsion bar, non-locking | n/a |
| total weight | 2600 kg | n/a |
| Load capacity | 2170 kg | n/a |
| Curb weight | 430 kg | n/a |
| Overall dimensions, max | 4000*2000 mm | n/a |
| Platform size, max. | 2500*1500 mm | n/a |
| Frame | Welded volumetric steel frame-type structure with cross members reinforced with gussets | n/a |
| Drawbar | Straight | n/a |
| Protective coating | Powder coating, black | n/a |
| Set of attachments: |  |  |
| Axle | Rigid, non-braking, 1300 kg | 2 |
| Coupling device | NATO loop or coupling device under the ball | 1 |
| Support stand | 900 kg | 4 |
| Support stand | 900 kg | 4 |
| Anti-roll bar | For locking wheels when parked | 2 |
| Mudguards | Plastic | 3 |
| Wheels | R14C | 6 |
| Reflectors | Reflectors (triangular, yellow, white) in accordance with the requirements of UNECE Regulation 48-03 set | set |

1.3.3 Technical requirements for Automatic Transfer Switch Board (ATS Panel):

The wall-mounted Automatic Transfer Switch Board (1 unit) must be equipped with the following components:

- Incoming load circuit breakers with overload and short-circuit protection functions

- Surge protection device (SPD) for protection against impulse overvoltage

- Protective front panels.

Technical specifications:

- Rated voltage: Un = 400 V

- Rated current: In = 100 A

- Maximum dimensions: H × W × D: 1000 × 600 × 200 mm

- Enclosure protection rating: IP41

Note:

- Incoming power cables must enter from the top.

- Outgoing feeder lines must exit from the bottom.

List of main components:

| Name | Quantity |
| --- | --- |
| Automatic circuit breaker 100A 3P (16 kA) | 2 |
| Surge arrester T12 280/12.5 4+0 | 1 |
| Motorized load transfer switch 4×125A | 1 |
| Automatic transfer switch (ATS) controller | 1 |
| Outdoor metal enclosure | 1 |
| Set of additional materials (signal indicators, busbars, terminals, fuses, labelling, cable lugs, cabling and wiring products, etc.) | 1 |

The assembly of electrical switchboards shall be carried out using electrotechnical components from leading manufacturers (Schneider Electric, ETI, Socomec, Phoenix Contact, Legrand, ABB, Siemens).

### The Supplier’s Technical Specifications

The Supplier must provide a table of correspondence of the proposed solution with the manufacturer and model to the technical specification.

[insert reference to attachment and/ or insert a description]

Signature

I, the undersigned, hereby declare that:

- I am empowered to represent the tenderer with mandate to establish a legal obligation on behalf of the tenderer in relation to the Buyer.

- I have familiarised myself with the information available to date concerning this tender procedure.

- The submitted tender is fully compliant with all requirements and that all statements, descriptions, etc. provided by the Seller in this Appendix 1 are accurately and correct.

- The statements in this Appendix 1, including attached Technical Specifications, take precedence over the Supplier’s other statements and/ or indications in the tender, if any.

- The submitted tender will be deemed to be the property of the Buyer.

| Name | [insert name of the undersigned] |
| --- | --- |
| Position | [insert name of the undersigned] |
| Date | [insert date] |
| Signature |  |